## Scope

This leaflet contains general procedures to be followed from the time the transformer and its accessories are received, until it is put into operation.  These instructions do not purport cover all possible contingencies that may arise during installation, operation, or maintenance, and all details and variations of this equipment.  If you require additional information regarding this equipment, contact  ABB Small Power Transformers in South Boston, Virginia.

The theoretically ideal conditions for paralleling transformers are:

- Identical turn ratios and voltage ratings.

- Equal percent impedances.

- Equal ratios of resistance to reactance.

- Same polarity.

- Same phase angle shift.

- Same phase rotation.

## Single-Phase Transformers

For single-phase transformers, only the first four conditions apply, as there is no phase rotation or phase angle shift due to voltage transformation.

If the turns ratio are not same a circulating current will flow even at no load.  If the percent impedance or the ratios of resistance to reactance are different there will be no circulating current at no load, but the division of load between the transformers when applied will no longer be proportional to their KVA ratings.

## Three-Phase Transformers

The same conditions hold true for three phase transformers except that in this case the question of phase rotation and phase angle shift must be considered.

## Phase Angle Shift

Certain transformer connections as the wye-delta or wye-zigzag produce a 30º shift between the line voltages on the primary side and those on the secondary side.  Transformers with these connections cannot be paralleled with other transformers not having this shift such as wye-wye, delta-delta, zigzag-delta, or zigzag-zigzag.

Phase Rotation

Phase rotation refers to the order in which the terminal voltages reach their maximum values.  In paralleling, those terminals whose voltage maximums occur simultaneously are paired.

Power Transformer Practice

The preceding discussion covered the theoretically ideal requirements for paralleling.  In actual practice, good paralleling can be accomplished although the actual transformer conditions deviate by small percentages from the theoretical ones.

Good paralleling is considered attainable when the percentage impedances of two winding transformers are within 7.5% of each other.  For multi-winding and auto-transformers, the generally accepted limit is 10%.

Furthermore, in power transformers of normal design the ratio of resistance to reactance is generally sufficiently small to make the requirement of equal ratios of negligible importance in paralleling.

When it is desired to parallel transformers having widely different impedances, reactors or auto-transformers having the proper ratio should be used.  If a reactor is used it is placed in series with the transformer whose impedance is lower.  It should have a value sufficient to bring the total effective percent impedance of the transformer plus the reactor up to the value of the percent impedance of the second transformer.

When an auto-transformer is used, the relative currents supplied by each transformer are determined by the ratio of the two sections of the auto-transformer.  The auto-transformer adds a voltage to the voltage drop in the transformer with the lower impedances and subtracts a voltage from the voltage drop in the transformer with the higher impedance.  Auto-transformers for use in paralleling power transformers are specially designed for each installation.  The wiring diagram showing the method of connecting the auto-transformer is usually furnished.

In general, transformers built to the same manufacturing specifications as indicated by the nameplate may be operated in parallel.

Connecting transformers in parallel when the low voltage tension is comparatively low requires care that the corresponding connecting bars or conductors have approximately the same impedance.  If they do not, the currents will not divide properly.

Renewal Parts

Contact ABB Small Power Transformers in South Boston, Virginia, for repair and replacement information at (434) 572 – 5695.

Disclaimer of Warranties and Limitation of Liability

THERE ARE NO UNDERSTANDINGS, AGREEMENTS, REPRESENTATIONS, OR WARRANTIES, EXPRESSED OR IMPLIED, INCLUDING WARRANTIES OF MERCHANTABILITY OR FITNESS FOR A PARTICULAR PURPOSE OTHER THAN THOSE SPECIFICALLY SET OUT BY AN EXISTING CONTRACT BETWEEN THE PARTIES.  ANY SUCH CONTRACT STATES THE ENTIRE OBLIGATION OF THE SELLER.  THE CONTENTS OF THIS DOCUMENT SHALL NOT BECOME PART OF OR MODIFY ANY PRIOR OR EXISTING AGREEMENT, COMMITMENT OR RELATIONSHIP.  The information, recommendations, description and safety notations in this document are based on our experience and judgment with respect to Transformers.  THIS INFORMATION SHOULD NOT BE CONSIDERED TO BE ALL INCLUSIVE OR COVERING ALL CONTINGENCIES.  If further information is required, ABB Inc. should be consulted.

NO WARRANTIES, EXPRESSED OR IMPLIED, INCLUDING WARRANTIES FOR FITNESS FOR A PARTICULAR PURPOSE OR MERCHANTABILITY, OR WARRANTIES ARISING FROM COURSE OF DEALING OR USAGE OF TRADE ARE MADE REGARDING THE INFORMATION, RECOMMENDATIONS, DESCRIPTIONS, AND SAFETY NOTATIONS CONTAINED HEREIN.  In no event will ABB Inc. be responsible to the user in contract, in tort (including negligence), strict liability or otherwise for any special, indirect, incidental or consequential damage or loss whatsoever including but not limited to damage to or loss of use of equipment, plant or power system, cost of capital, loss of profits or revenues, cost of replacement power, additional expenses in the use of existing power facilities, or claims against the user by its customers resulting from the use of the information,  recommendations, description and safety notations contained herein.